## Mass_Energy Balance
[8 empty] | cold | hot | cold | hot | cold | hot |  | a[4] + T*(a[3] + T*(a[2] + T*a[1]))
[6 empty] | 6627.7773 | -7717.5127 | 4197.52 | 4195.2007 | 7.3328 | 80 | 280.4828 | 353.15 | 4197.5201 | -7.9613e-05 | 0.090325 | -33.1869 | 8156.6624
|  | HX01 | HX02 | HX03 | HX03 | 6798.5244 | -7524.7173 | 4196.0576 | 4192.9453 | 8.4746 | 77.0695 | 281.6246 | 350.2194 | 4196.0578
COLD | d T | 8.6 | 8.6 | 8.6 | 8.6 | 6973.503 | -7336.5117 | 4194.62 | 4190.8257 | 9.6462 | 74.2106 | 282.7962 | 347.3606 | 4194.6199
| cp | 4198.5741 | 4198.5741 | 4198.5741 | 4198.5741 | 7152.801 | -7152.8057 | 4193.2095 | 4188.847 | 10.8484 | 71.4218 | 283.9984 | 344.5718 | 4193.2094
| m_flow | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 7336.5073 | -6973.508 | 4191.8296 | 4187.0127 | 12.0819 | 68.7016 | 285.2319 | 341.8516 | 4191.8298
[6 empty] | 7524.7124 | -6798.5293 | 4190.4844 | 4185.3267 | 13.3475 | 66.0485 | 286.4975 | 339.1985 | 4190.4845
| Pt | 50131.3327 | 50131.3327 | 50131.3327 | 50131.3327 | 7717.5073 | -6627.7817 | 4189.1772 | 4183.7915 | 14.646 | 63.4609 | 287.796 | 336.6109 | 4189.1771
| Pt (kW) | 50.1313 | 50.1313 | 50.1313 | 50.1313 | 50131.3327 | -50131.3664 | 4187.9116 | 4182.4097 | 15.9781 | 60.9375 | 289.1281 | 334.0875 | 4187.9115
|  | HX01 | HX02 | HX03 | HX03
HOT | d T | 20 | 20 | 20 | 20
| cp | 4161.0729 | 4161.0729 | 4161.0729 | 4161.0729
| m_flow | 0.60238 | 0.60238 | 0.60238 | 0.60238
| Pt | 50131.3327 | 50131.3327 | 50131.3327 | 50131.3327 | 4198.5741 | 4161.0729
| Pt (kW) | 50.1313 | 50.1313 | 50.1313 | 50.1313
HH_CH4 | 55.5 | MJ/kg
m_H2O | 1.8072 | kg/s
m_CH4 | 0.002785 | kg/s
m_H2O | 2.4095 | kg/s
m_CH4 | 0.0037117 | kg/s

## Only Boiler
[8 empty] | cold | hot | cold | hot | cold | hot |  |  | a[4] + T*(a[3] + T*(a[2] + T*a[1]))
[6 empty] | 6627.7773 | -7717.5127 | 4197.52 | 4195.2007 | 7.3328 | 80 | 280.4828 | 353.15 | 4197.5201 |  | -7.9613e-05 | 0.090325 | -33.1869 | 8156.6624
|  | HX01 | HX02 | HX03 | HX03 | 6798.5244 | -7524.7173 | 4196.0576 | 4192.9453 | 8.4746 | 77.0695 | 281.6246 | 350.2194 | 4196.0578
COLD | d T | 8.6 | 8.6 | 8.6 | 8.6 | 6973.503 | -7336.5117 | 4194.62 | 4190.8257 | 9.6462 | 74.2106 | 282.7962 | 347.3606 | 4194.6199
| cp | 4198.5741 | 4198.5741 | 4198.5741 | 4198.5741 | 7152.801 | -7152.8057 | 4193.2095 | 4188.847 | 10.8484 | 71.4218 | 283.9984 | 344.5718 | 4193.2094
| m_flow | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 7336.5073 | -6973.508 | 4191.8296 | 4187.0127 | 12.0819 | 68.7016 | 285.2319 | 341.8516 | 4191.8298
[6 empty] | 7524.7124 | -6798.5293 | 4190.4844 | 4185.3267 | 13.3475 | 66.0485 | 286.4975 | 339.1985 | 4190.4845
| Pt | 50131.3327 | 50131.3327 | 50131.3327 | 50131.3327 | 7717.5073 | -6627.7817 | 4189.1772 | 4183.7915 | 14.646 | 63.4609 | 287.796 | 336.6109 | 4189.1771
| Pt (kW) | 50.1313 | 50.1313 | 50.1313 | 50.1313 | 50131.3327 | -50131.3664 | 4187.9116 | 4182.4097 | 15.9781 | 60.9375 | 289.1281 | 334.0875 | 4187.9115
|  | HX01 | HX02 | HX03 | HX03
HOT | d T | 20 | 20 | 20 | 20
| cp | 4161.0729 | 4161.0729 | 4161.0729 | 4161.0729
| m_flow | 0.60238 | 0.60238 | 0.60238 | 0.60238 | [7 empty] | Circuit
| Pt | 50131.3327 | 50131.3327 | 50131.3327 | 50131.3327 | 4198.5741 | 4161.0729
| Pt (kW) | 50.1313 | 50.1313 | 50.1313 | 50.1313 | [7 empty] | Gas Boiler |  | Pump P101 |  | Valve V101 |  | Pump P901 |  | Valve V901 |  | HX01 |  | HX02 |  | HX03 |  | HX04
[13 empty] | In | Out | In | Out | In | Out | In | Out | In | Out | In Hot | Out Cold | In Hot | Out Hot | In Hot | Out Hot | In Hot | Out Hot
p
HH_CH4 | 55.5 | MJ/kg | [9 empty] | T | 70.5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 70.4522 | 80 | 70.4522 | 80 | 70.4522 | 80 | 70.4522
[12 empty] | cp | 4182 | [9 empty] | 4161.0729 |  | 4161.0729 |  | 4161.0729 |  | 4161.0729
[12 empty] | m_flow | 2.5 |  | 2.5 |  | 2.5 |  | 2.5 |  | 2.5 |  | 0.625 |  | 0.625 |  | 0.625 |  | 0.625
m_H2O | 1.8072 | kg/s | [9 empty] | Pt_source | 99.3225 | [9 empty] | 24.8306 |  | 24.8306 |  | 24.8306 |  | 24.8306
m_CH4 | 0.002785 | kg/s | [9 empty] | Pt_demand | [10 empty] | -24.8306 |  | -24.8306 |  | -24.8306 |  | -24.8306
[12 empty] | m_flow | [10 empty] | 1.75 |  | 1.75 |  | 1.75 |  | 1.75
[12 empty] | cp | [10 empty] | 4198.5741 |  | 4198.5741 |  | 4198.5741 |  | 4198.5741
m_H2O | 2.4095 | kg/s | [9 empty] | T | [10 empty] | 8 | 11.3795 | 8 | 11.3795 | 8 | 11.3795 | 8 | 11.3795
m_CH4 | 0.0037117 | kg/s | [20 empty] | In Cold | Out Cold | In Cold | Out Cold | In Cold | Out Cold | In Cold | Out Cold
[23 empty] | HX01 |  | HX02 |  | HX03 |  | HX04
Pt = mcp(Tin-Tout)
Tin - Pt/mcp
|  | HX01 | HX02 | HX03 | HX03
|  | kW | kW | kW | kW
COLD | Pt (kW) | 25 | 25 | 25 | 25
| cp | 4198.5741 | 4198.5741 | 4198.5741 | 4198.5741
HOT | d T | 20
| cp | 4.1611
| m_flow | 1.2048
| Pt (kW) | 100.2627
[31 empty] | q(m3/h) | mh2o | w(kg/s) | dp (Pa) | dp (bar)
[31 empty] | 0 | 0 | 0 | 0 | 0
[31 empty] | 7 | 0.1 | 1.925 | 980.665 | 0.0098067
[31 empty] | 13 | 0.2 | 3.575 | 1961.33 | 0.019613
[31 empty] | 18 | 0.3 | 4.95 | 2941.995 | 0.02942
[31 empty] | 22 | 0.4 | 6.05 | 3922.66 | 0.039227
[31 empty] | 34 | 0.8 | 9.35 | 7845.32 | 0.078453
[31 empty] | 38 | 0.95 | 10.45 | 9316.3175 | 0.093163
[31 empty] | 40 | 1.025 | 11 | 10051.8162 | 0.10052

## GBoiler & ElectricB
[6 empty] | 6627.7773 | -7717.5127
|  | HX01 | HX02 | HX03 | HX03 | 6798.5244 | -7524.7173
COLD | d T | 8.6 | 8.6 | 8.6 | 8.6 | 6973.503 | -7336.5117
| cp | 4198.5741 | 4198.5741 | 4198.5741 | 4198.5741 | 7152.801 | -7152.8057
| m_flow | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 7336.5073 | -6973.508
[6 empty] | 7524.7124 | -6798.5293
| Pt | 50131.3327 | 50131.3327 | 50131.3327 | 50131.3327 | 7717.5073 | -6627.7817
| Pt (kW) | 50.1313 | 50.1313 | 50.1313 | 50.1313 | 50131.3327 | -50131.3664
|  | HX01 | HX02 | HX03 | HX03
HOT | d T | 20 | 20 | 20 | 20
| cp | 4161.0729 | 4161.0729 | 4161.0729 | 4161.0729
| m_flow | 0.60238 | 0.60238 | 0.60238 | 0.60238
| Pt | 50131.3327 | 50131.3327 | 50131.3327 | 50131.3327 | 4198.5741 | 4161.0729
| Pt (kW) | 50.1313 | 50.1313 | 50.1313 | 50.1313 |  |  |  | Electric Boiler |  | Pump P401 |  | Valve V401 |  | Gas Boiler |  | Pump P101 |  | Valve V101 |  | Pump P901 |  | Valve V901 |  | HX01 |  | HX02 |  | HX03 |  | HX04
[9 empty] | In | Out | In | Out | In | Out | In | Out | In | Out | In | Out | In | Out | In | Out | In Hot | Out Cold | In Hot | Out Hot | In Hot | Out Hot | In Hot | Out Hot
p
HH_CH4 | 55.5 | MJ/kg | [5 empty] | T | 70.5 | 80 | 80 | 80 | 80 | 80 | 70.5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 70.4522 | 80 | 70.4522 | 80 | 70.4522 | 80 | 70.4522
[8 empty] | cp | 4182 | [5 empty] | 4182 | [9 empty] | 4161.0729 |  | 4161.0729 |  | 4161.0729 |  | 4161.0729
[8 empty] | m_flow | 1.2585 |  | 1.2585 |  | 1.2585 |  | 2.5 |  | 2.5 |  | 2.5 |  | 3.7585 |  | 3.7585 |  | 0.93963 |  | 0.93963 |  | 0.93963 |  | 0.93963
m_H2O | 1.8072 | kg/s | [5 empty] | Pt_source | 50 | [5 empty] | 99.3225 | [9 empty] | 37.3306 |  | 37.3306 |  | 37.3306 |  | 37.3306
m_CH4 | 0.002785 | kg/s | [5 empty] | Pt_demand | [16 empty] | -37.3306 |  | -37.3306 |  | -37.3306 |  | -37.3306
[8 empty] | m_flow | [16 empty] | 1.75 |  | 1.75 |  | 1.75 |  | 1.75
[8 empty] | cp | [16 empty] | 4198.5741 |  | 4198.5741 |  | 4198.5741 |  | 4198.5741
m_H2O | 2.4095 | kg/s | [5 empty] | T | [16 empty] | 8 | 13.0807 | 8 | 13.0807 | 8 | 13.0807 | 8 | 13.0807
m_CH4 | 0.0037117 | kg/s | [22 empty] | In Cold | Out Cold | In Cold | Out Cold | In Cold | Out Cold | In Cold | Out Cold
[25 empty] | HX01 |  | HX02 |  | HX03 |  | HX04
Pt = mcp(Tin-Tout)
Tin - Pt/mcp
|  | HX01 | HX02 | HX03 | HX03
|  | kW | kW | kW | kW
COLD | Pt (kW) | 25 | 25 | 25 | 25
| cp | 4198.5741 | 4198.5741 | 4198.5741 | 4198.5741 |  |  |  | Electric Boiler |  | Pump P401 |  | Valve V401 |  | Gas Boiler |  | Pump P101 |  | Valve V101 |  | Pump P901 |  | Valve V901 |  | HX01 |  | HX02 |  | HX03 |  | HX04
[9 empty] | In | Out | In | Out | In | Out | In | Out | In | Out | In | Out | In | Out | In | Out | In Hot | Out Cold | In Hot | Out Hot | In Hot | Out Hot | In Hot | Out Hot
p
HOT | d T | 20 | [5 empty] | T | 65 | 80 | 80 | 80 | 80 | 80 | 65 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 64.9246 | 80 | 64.9246 | 80 | 64.9246 | 80 | 64.9246
| cp | 4.1611 | [5 empty] | cp | 4182 | [5 empty] | 4182 | [9 empty] | 4161.0729 |  | 4161.0729 |  | 4161.0729 |  | 4161.0729
| m_flow | 1.2048 | [5 empty] | m_flow | 0.79707 |  | 0.79707 |  | 0.79707 |  | 2.3 |  | 2.3 |  | 2.3 |  | 3.0971 |  | 3.0971 |  | 0.77427 |  | 0.77427 |  | 0.77427 |  | 0.77427
[8 empty] | Pt_source | 50 | [5 empty] | 144.279 | [9 empty] | 48.5698 |  | 48.5698 |  | 48.5698 |  | 48.5698
| Pt (kW) | 100.2627
[8 empty] | Pt_demand | [16 empty] | -48.5697 |  | -48.5697 |  | -48.5697 |  | -48.5697
[8 empty] | m_flow | [16 empty] | 1.75 |  | 1.75 |  | 1.75 |  | 1.75
[8 empty] | cp | [16 empty] | 4198.5741 |  | 4198.5741 |  | 4198.5741 |  | 4198.5741
[8 empty] | T | [16 empty] | 8 | 14.6104 | 8 | 14.6104 | 8 | 14.6104 | 8 | 14.6104
[25 empty] | In Cold | Out Cold | In Cold | Out Cold | In Cold | Out Cold | In Cold | Out Cold
[25 empty] | HX01 |  | HX02 |  | HX03 |  | HX04
Pt = mcp(Tin-Tout)
Tin - Pt/mcp

## HeatPumps
| Tin_hot | Tout_hot | m_hot | Tin_cold | Tout_cold | m_cold |  |  |  | 20000 | 2.4444 | 8181.8182
EX601 | 17 |  |  |  | 14
| 17 | 14.7 | 4.1667 | 7 | 14 | 1.369 | 4.9286
|  |  |  | Tin_cold | Tout_cold | m_cold | Tin_hot | Tout_hot | m_hot
HP601 |  |  |  | 7 | 14 | 1.369 | 48.9205 | 45 | 2.4444
HP301
[7 empty] | 48.9205 | 45 | 2.4444 |  | 60 | 80 | 0.47917